THE OPERATION RESULT OF THE DEMONSTRATION OF FUEL CELLS AND ENERGY NETWORKS OF ELECTRICITY, HEAT, AND HYDROGEN AT AN APARTMENT BUILDING – 
THE SECOND REPORT

H. Aki1, Y. Taniguchi1, J. Kondoh1, I. Tamura2, A. Kegasa2, 
Y. Ishikawa3, S. Yamamoto3, I. Sugimoto3

1. Introduction

The concept of interconnecting a group of residential homes by energy networks involving electricity, heat (hot water), and hydrogen, with some of these homes possessing fuel cells, has previously been proposed [1,2]. The networks connect fuel cell stacks, fuel processors, and other equipment, and are expected to contribute to the mitigation of the associated environmental impacts through the flexible and efficient utilization of the equipments. Starting with small-scale systems, a gradual expansion to larger systems can be achieved by consistently using conventional energy systems; this can also help to avoid a large initial investment.

The energy interchange system has also been proposed for apartment houses. The combination of two different types of distributed generations (DGs)—proton exchange membrane fuel cells (PEMFC, or polymer electrolyte fuel cells [PEFC]) and gas engines/solid oxide fuel cells (SOFC)—allows variations in the ratio of heat to electricity supply and enables load matching, which is necessary for the homes. We have developed mathematical models, a PC-based simulator, and an experimental system to evaluate the proposal [2]. The effects of the systems were analyzed and verified by the simulator and experimental systems.

As the next step towards a practical application, a demonstration has been started in existing residential homes to evaluate the proposal since April 2007. The demonstration is presented in a small apartment building with 18 apartments, which was constructed for experimental purpose in Osaka, Japan. Two homes on the 3rd floor and four homes on the 4th floor, total six homes are involved to the demonstration. The six families are spending their completely normal daily life using the system. Three small PEM fuel cells with hot water tanks have been installed, and the electricity and hot water from the fuel cells are shared via an internal electricity grid and a hot water pipe. Hydrogen production facility, a small storage and a hydrogen pipe have been installed as an infrastructure to supply hydrogen to the fuel cells. The energy flow process from hydrogen production to consumption in homes is demonstrated. The operation results in fall of 2007 and lessons learned are reported.

2. Proposed Systems

The Japanese government has initiated a large-scale deployment for the project of the residential fuel cell systems in 2005. More than 2,000 units have been installed by 2007, i.e. the residential fuel cells are commercially available in Japan. They are PEMFCs which have capacities of 700–1000 W for electricity generation and are designed to be combined with fuel processors to produce hydrogen from natural gas (methane) or kerosene. Those commercialized residential fuel cells have some challenges in terms of efficient operation as follows.

The first challenge is the demand characteristics of residential homes. The installation of fuel cells with capacities that equal or exceed the peak demand is not economically justified. Therefore, the capacity of the commercialized residential fuel cells is 700–1000 W, and they are operated in a grid dependent mode and are not intended to supply the peak demand.

Residential homes have a varying energy demand in general. The electricity base load of Japanese homes is usually 250 to 500 W, and their peak load is 3 to 5 kW. Their electricity demands have “demand spikes”, which is a large load in a short period, such as that is caused by the use of microwaves. The load factors of the electricity demands are usually low because of the demand spikes. The demand spikes usually occur at different times for different homes. The maximum load of the combined load of all the homes is considerably smaller than the sum of the peak load values of each home. For a group of homes, combining the electricity load of all the homes and considering them as a single consumer reduces the required total capacity of the equipment including fuel cells.

The fuel processors, which produce hydrogen from natural gas (methane) or kerosene, are equipped to the fuel cell systems so that any hydrogen infrastructure is not necessary. However, the shortcoming of that scheme is slow response to demand. The fuel processors use chemical process and have four different catalyses that must be kept different temperatures. They can not respond to changes in the load quickly, while the fuel cell stacks can respond quickly and without delay, i.e., the fuel cells have the ability to respond to the spike in electricity demand. Addition to the slow response, the fuel processors provide lower efficiency at partial load operation and require 1 hour or longer preheating of catalyses at start-up. These shortcomings spoil the advantages of the fuel cell stacks.

Based on the above discussions, authors have designed and proposed typical system configurations for detached houses and apartment buildings. The implementation of the energy networks for the group enables connects the equipment and the energy demand of the homes, and enables a coordinated and flexible operation of the equipment.

An example of the system configurations for a group of eight detached houses is shown in Figure 1. The electricity generated from the fuel cells, which are installed in residential homes, can be shared via a grid because the fuel cells are interconnected with the grid. This means that the homes virtually share all the fuel cells.

It is better to install small fuel cells in each home than to install a single large fuel cell in only one of them. The exhaust heat from the fuel cells should be recovered and used to increase the total energy efficiency. Hot water from the heat exchangers of the fuel cells should primarily be used in homes where fuel cells are installed; otherwise, the hot water has to be wasted or transported to other homes, and the total efficiency will be decreased.

Figure 2 shows an example of an apartment building which has 100 apartments (10 x10). In the case of an apartment building, it is possible to install larger systems into public rooms such as the electric room of the apartment building. A hybrid generation system, which combines two or more types of generation systems, e.g., PEMFCs and SOFCs, enables variations in the ratio of heat to electricity supply depending on the demand. The authors propose the installation of PEMFCs into some of the apartments along with the installation of a gas engine or an SOFC.

Centralized hydrogen production with purifiers (pressure swing adsorption [PSA] units) will be chosen for the apartment buildings. It can provide pure hydrogen and is better suited for fuel cell stack operation; however, it is unavailable for detached houses due to technical constraints in PSA production. The minimum capacity of a PSA unit is 5–10 Nm3/h, which is equivalent to 5–10 kW capacity of fuel cell stacks.

In these apartment buildings, the hot water will be circulated horizontally and will be shared between all houses on the same floor. Sharing the hot water between all the houses in the building would be another option; this would depend on the trade-off between the electricity consumption involved in pumping up the water and its utilization.

3. Demonstration Project

The purpose of the demonstration project is as follows: 1) to evaluate consumer acceptance of hydrogen based system, 2) to improve operational algorithms to adapt to more practical applications, and 3) to verify the effect of the proposed systems on the reduction of primary energy consumption and CO2 emission.

The demonstration is being conducted at Experimental Complex NEXT21 [3] in Osaka, Japan. It is an apartment building which has seven storeys including a basement and 18 families are living on 3rd–6th floors The allocated rooms are completely separated from each other to simulate detached houses. Each floor has a large space for the installation of pipes for hot water and gas supply and for electric cables beneath the floor.

Two homes on 3rd floor and four homes on 4th floors are involved in the demonstration project. A hydrogen production facility (reformer + PSA, 1.5Nm3/h each) and a small storage tank are installed on the roof of the building. Hydrogen pipes are installed for the entire area involved in the demonstration; hydrogen is supplied as part of the basic infrastructure such as electricity and water. Therefore, the operation of the hydrogen production facility may be beyond the scope of the evaluation in this demonstration. A PEMFC and two PEMFCs are installed on 3rd and 4th floors. Hot water tanks are installed adjacent to the fuel cell stacks to use the recovered heat for production of hot water. The hot water is transported through a pipe. Auxiliary boilers are provided to all six homes as a backup.

Figure 3 represents the implemented energy systems. The major specifications of the fuel cells and the hot water tanks are shown in Table 1. According to our measurement, the efficiencies of electricity and heat generations are approximately 40 %, while the design efficiencies are as shown in the table. Note that the electricity generation efficiencies depend not only on fuel cell stack characteristics but also on inverter performances.

Two types of demonstrations are performed as follows.

Detached house case: A simulation of the system for a group of detached homes. Four homes on 4th floor are involved. Two of four homes have PEMFCs. Electricity and hot water are interchanged or shared. Hot water interchange is also available between two tanks if necessary.

Apartment building case: A simulation of the system for an apartment building. The PEMFCs and hot water tanks are shared. Two hot water tanks on the 4th floor are connected sequentially and used as single tank. Electricity is shared with all six homes and hot water is circulated and shared with two/four homes on each floor.

The energy demand of the homes that includes electricity consumption for air conditioning and lighting, hot water consumption for bathing etc., as well as the status of the equipment and energy flow are measured every 2 seconds and stored on a server via Ethernet.

The demonstration is conducted for three weeks in every season (spring, summer, fall, winter) by following order: 1) energy demand measurement without fuel cells – to be evaluation standards, 2) detached house case, 3) apartment building case.

Various operational strategies can be applied to the fuel cell stacks and other equipment. The objective would be the minimization of cost, CO2 emission, and primary energy. There are also challenges with regard to the operation such as to balance the electricity and hot water supply to the demand, or to improve operational algorithm for practical application.

4. Demonstration Result

The entire system has functioned well; no major fault or trouble has been happened since the demonstration started. Hydrogen production facility and fuel cells had some minor troubles, but they have been fixed. Most of them are not mechanical issues and only parameters adjustment was required.

The result of the fall of 2007 has been analyzed by present and reported in this paper.

The examples of operation results are compared in Table 2. Each column corresponds to a specific day in fall; conditions are not same, e.g., people’s behaviour and their energy demands vary day by day. Note that only four homes are involved to detached house case and all six homes are involved to apartment building case.

Most of electricity and hot water demands were supplied by fuel cells in both cases. The hot water demand of the apartment building case was significantly larger than that of the detached house case (almost doubled in per household), since the ambient temperature when the apartment building case was conducted was low. The hot water from fuel cells is almost in proportion to electricity from the fuel cells, and was not enough to cover all hot water demand in apartment building case; three 700 kW fuel cells are not enough. The auxiliary boilers compensated the shortage and supplied half of hot water demand. The average efficiencies of the fuel cells are calculated from Table 2; approximately 40% for both electricity and heat recovery.

86% and 59% of external energy supply was hydrogen, i.e. the apartments depended most of their end-use energy on hydrogen. Therefore, CO2 emission, energy cost, and other performance depend on hydrogen production in hydrogen energy systems.

The supply and demand of electricity and hot water including the operation of equipment of two cases are shown in Figures 4 and 5. The fuel cells followed to the demand variations in low demand hours, and are kept rated output in other hours. This confirms that PEMFC without fuel processor has enough loads following ability if high load response performance inverters are equipped. The fuel cells did not keep rated output in Figure 5(a) because of minor trouble on their control software. Figure 5(b) shows that the hot water from the fuel cells was not enough especially in evening to night as the demand was large.

5. Conclusion

The concepts of the proposed systems and the outline and present state of the demonstration project at an apartment building that hydrogen energy system is installed are presented in this paper. Hydrogen production facility is installed on the roof and hydrogen is supplied as a basic energy infrastructure in the building. Three PEMFCs are installed and supply electricity and hot water to six apartments.

The system is successfully running well. Hydrogen energy system is realized and shows that hydrogen fuelled homes are technologically available at present; 86% and 59% of end-use energy is supplied from hydrogen. However, they have still lifetime and cost issues.

The demonstration will be continued also in 2008 and is expected to provide more valuable data and lessons learned.

6. References

1.	Hirohisa Aki, et al.: Operational Strategies of Networked Fuel Cells in Residential Homes, IEEE Transactions on Power Systems Vol. 21, No. 3, 2006.

2.	Hirohisa Aki, et al.: Fuel Cells and Energy Networks of Electricity, Heat, and Hydrogen in Residential Areas, International Journal of Hydrogen Energy Vol. 31, No. 8, pp.967–980, 2006.

3 Toru Shiba: Experimentations at Experimental Complex NEXT21 (in Japanese), Energy and Resources, Japan Society of Energy and Resources, Vol. 28, No. 5, pp. 342-345, 2007.

# Text boxes

1 National Institute of Advanced Industrial Science and Technology (AIST)

2 Osaka Gas Co., Ltd.

3 KRI inc.

(a) Detached house case (boilers are for backup only.)

(b) Apartment house case (boilers are for backup only.)

Figure 3. Energy systems of the demonstration

Table 1 Specifications of fuel cells and hot water tanks

Figure 1. Example of the proposed system for a group of detached houses

Table 2 Energy supply and demand on specific days in fall 2007

Figure 2. Example of the proposed system for an apartment building (10 x 10 = 100)

(a) Electricity supply demand (2 PEMFC + 4 homes, 4th floor)

(b) Hot water supply and demand (1 tank + 2 homes, 4th floor)

Figure 4. Detached house case

(a) Electricity supply demand (3 PEMFCs + 6 homes, 3rd+4th floors)

(b) Hot water supply and demand (1 tank + 4 homes, 4th floor)

Figure 5. Apartment building case